## Slide 1: ML-Enhanced Partial Discharge Fault Detection in Covered Conductors
Jeffrey Egan // September 2022

## Slide 2: Overview
Background Information on the Project
Quick Exploratory Data Analysis
Primer on Partial-Discharge Faults
Data Preparation – Signal Processing
Feature Extraction and Features Analysis
Machine Learning Models and Deep Learning Networks
Model Evaluation and Performance Results
Interesting Observations, Lessons Learned
Ideas for Improving / Expanding upon this Project

## Slide 3: Partial Discharge Faults – Background & Motivation
Overhead, medium-voltage power lines run for hundreds of miles. These great distances make it expensive to manually inspect for damage that doesn't immediately lead to a power outage.
Degradation or rupturing of insulation systems can lead to a phenomenon known as partial discharge — an electrical discharge which does not bridge the electrodes between an insulation system completely.
Partial discharges slowly damage the power line. Left unrepaired they will eventually lead to a power outage, additional damage, and possibly even start a fire.
Meters employed to collect voltage data
Detect PD-Faults to enable proactive maintenance, avoiding service outages and reducing cost
Notes: Overhead power lines run for hundreds of miles to supply power to cities. These great distances make it expensive to manually inspect the lines for damage that doesn't immediately lead to a power outage (like tree branches falling on lines).
These modes of damage lead to a phenomenon known as partial discharge — an electrical discharge which does not bridge the electrodes between an insulation system completely.
Partial discharges slowly damage the power line, so left unrepaired they will eventually lead to a power outage or start a fire.
The challenge is to detect partial discharge patterns in signals acquired from these power lines with a new meter designed at the ENET Centre at VŠB. Effective classifiers using this data will make it possible to continuously monitor power lines for faults – helping to reduce maintenance costs and prevent power outages.
Solid Dielectric Loadbreak Switch

## Slide 4: Sample Measurements with 3 Phase Signals
Each signal (phase) contains 800,000 measurements of a power line’s voltage, taken over 20 milliseconds.
For signal processing, that means each signal data set has a sample rate of 40 million samples per second.
The underlying electric grid operates at 50Hz, this means each signal covers a single complete grid cycle.

## Slide 5: Quick EDA Reveals Highly Unbalanced Data
All Provided Data: Labeled & Unlabeled
  Labeled Training Set: 2,904 Measurements = 8,712 Signals (only 30% of data is labeled)
  Unlabeled Test Set: Perform Binary Classification: 6,779 Measurements = 20,337 Signals
Occurrence of Faults and Non-Faults in Labeled Data
  8187 Signals without Fault, 213 Signals with Fault (only 2.5% of labeled signals have faults!)
Grouping of Signal Faults per Measurement
  Measurements with no faults present: 2710 (93.3% of measurements exhibit no fault)
  Measurements with fault present in only 1 phase: 19 (9.7% of cases where faults present)
  Measurements with faults present in 2 of 3 phases: 19 (9.7% of cases where faults present)
  Measurements with faults present in all 3 phases: 156 (80.4% of cases where faults present)

## Slide 6: Detecting Partial Discharges is Difficult
PD Pattern Observed alongside other Noise Sources
Figure from Reference [1]
Many other sources of noise could be falsely attributed to partial discharge.
Ambient and Amplifier Noise
PD: Partial Discharge Fault Pattern
DSI: Discrete Spectral Interference
  E.g. Radio Emissions, Power Electronics
RPI: Random Pulses Interference
  Lightning, Switching Operations, Corona

## Slide 7: Identifying and Canceling Corona Discharge Peaks
Corona Discharge Pulse Followed by Dumped Oscillation
Figure from Reference [1]
Spontaneous corona discharges occur naturally in high-voltage systems unless care is taken to limit the electric field strength.
A corona will occur when the strength of the electric field (potential gradient) around a conductor is high enough to form a conductive region, but not high enough to cause electrical breakdown or arcing to nearby objects.
A corona discharge is an electrical discharge brought on by the ionization of a fluid such as air surrounding a conductor that is electrically charged.
Identify and flag probable Corona discharge peaks to mitigate false positives

## Slide 8: Focus on Portions of the Sinusoid with Rising Amplitude for Improved PD Detection
Sections of Sinusoidal Shape (1,2) with the Statistically Highest Occurrence of PD pulses
Figure from Reference [2]
One of the most common fundamental features of the PD pattern is that it occurs on the rising amplitude edges of the sinusoidal curve.
During feature extraction, this allows omission of half of the signal data points – increasing processing efficiency.
Running feature extraction on the high-probable region also increases the model’s ability to detect true faults and avoid false positives.

## Slide 9: Data Preparation & Signal Processing
Raw Signal
Fit Sinusoid
Probable Region
De-Trend
Trimming
Feature Extraction
Denoising
Three signals per measurement, 800k samples / signal. Signals individually labeled.
Notes: Discrete Wavelet Transform to Remove Spectral Interference and Ambient Noise
  Daubechies 4 Wavelet (db4)
Fit a Sinusoidal Function to the DWT Signal and Detect the PD-Probable Region
Use an Nth Discrete Difference to De-Trend the Function
  First-order has proven sufficient
Perform Peak Detection and Subsequently Cancel of False Peaks
  Peak Detection using Fixed Amplitude Threshold
  Cancel High Amplitude Peaks, and Peaks Attributed to Corona Discharge

## Slide 10: Denoising – Remove DSI & Ambient Noise with DWT
Raw Signal
Fit Sinusoid
Probable Region
De-Trend
Trimming
Feature Extraction
Denoising
Discrete Wavelet Transform to Remove Spectral Interference and Ambient Noise – Daubechies 4 Wavelet (db4)

## Slide 11: Fit a Sinusoidal Function to the DWT Signal
Raw Signal
Fit Sinusoid
Probable Region
De-Trend
Trimming
Feature Extraction
Denoising
Fit a 50Hz sinusoid to the de-noised signal with a least squares approach
Notes: Generate your own 50Hz sinusoid, least_squares optimizer

## Slide 12: Use Rising Amplitude to Identify the PD-Probable Region
Raw Signal
Fit Sinusoid
Probable Region
De-Trend
Trimming
Feature Extraction
Denoising
Use first derivative to index the rising amplitude of the sinusoid and highlight the PD-probable region of the signal
Notes: Used np.gradient for first derivative

## Slide 13: Detrend Signal to Remove Sinusoidal Element
Raw Signal
Fit Sinusoid
Probable Region
De-Trend
Trimming
Feature Extraction
Denoising
Use an Nth Discrete Difference to De-Trend the Function – First Order was Sufficient
Notes: Avoids discontinuity from phase-wrap
Gives more significance to statistics like mean and variance
Calculate mean crossing and zero crossing
x = np.diff(signal, n=1, axis=-1) # Calculate the n-th discrete difference along the given axis

## Slide 14: Trim Signal to Only Look at the PD-Probable Region
Raw Signal
Fit Sinusoid
Probable Region
De-Trend
Trimming
Feature Extraction
Denoising
Discard the non-probable region, and trim the signal from 800k to 400k samples

## Slide 15: Perform Feature Extraction on Signal
Extraction Yields 36 Features
Mean
Standard Deviation
Variance
Mean + Std. Deviation
Mean - Std. Deviation
Max Range
Root Mean Square
Entropy
Number Crossings (mean & zero)
Percentiles [0, 1, 25, 50, 75, 99, 100]
Relative Percentiles (pctl. - mean)
Peak Counts (True, Cancelled)
Peak Statistics (mean/max height, width, etc)
Process the PD-Probable Region of the De-Trended, De-Noised Signal and Build a Feature Matrix to be used as Input to Machine Learning and Deep Learning Models.
Slice the signal into 400 parts (each 1000 samples in length)
Calculate and determine features per slice
Final Feature Array Shape: [8275, 36, 400]

## Slide 16: False Peaks Cancellation
False peaks…
  Reach much higher amplitude than the PD-pattern
  Were often followed by another large peak of opposite polarity, creating a nearly symmetric pair
  Have an identifiable “pulse trains” in the time domain.
From reviewing background literature on the subject [2], it was made clear that a statistically significant portion of the false positives in prior research were driven by false peaks.
Figure from Reference [1]
Signal without Fault, Before and After False Peak Cancellation

## Slide 17: Feature Exploration – Correlation Heat Map
Useful for a quick sanity check on extracted features. May also be used to identify redundant features.

## Slide 18: Feature Exploration – Pair Grids & PDF Estimates
3x3 Pair Grid to Show Detail
Scatters and KDE (probability density estimations)
Full Pair Grid
Notes: In statistics, kernel density estimation (KDE) is the application of kernel smoothing for probability density estimation

## Slide 19: Not All Features are Equally Influential
Later in the process, some features with minimal influence may be omitted to reduce the size of a model

## Slide 20: Machine Learning Approaches
k-Nearest Neighbors (k-NN)
  Monte Carlo over k parameter
Support Vector Machines (SVM)
  Radial Basis Function (rbf) kernel and Monte Carlo over gamma parameter.
Random Forest Decision Trees (RF)
  Regarded for handling unbalanced data when tuned properly.
Light Gradient Boosting Framework
  Powerful, tree-based learning algorithm that grows vertically (leaf-wise)
  Sensitive to overfitting on small data sets (<10,000 data points)
  In binary classification, model returns probability that a sample belongs to the positive class.

## Slide 21: Deep Learning Approaches
Recurrent Neural Network (LSTM)
  Signal length (400k) too excessive to feed directly without further processing (e.g. truncating, compressive sampling, or some encoder-decoder architecture).
  They can be adapted for classification but prior experience with LSTM models used for time series prediction
Convolutional Neural Network (CNN)
  Effective at pattern recognition and anomaly detection
  Simple CNN Model:
    Convolution layers (feature extraction)
    Pooling layers (decrease the size of convolved feature maps, summarizes features)
    Fully connected layers (flattening & classification)
    Dropout (mitigates overfitting when all features are fully connected
VSBNet
Notes: VSBNet(
(conv0a): Conv1d(36, 64, kernel_size=(4,), stride=(1,))
(conv0b): Conv1d(64, 64, kernel_size=(4,), stride=(1,))
(mp0): MaxPool1d(kernel_size=2, stride=2, padding=1, dilation=1, ceil_mode=False)
(conv1a): Conv1d(64, 20, kernel_size=(4,), stride=(1,))
(conv1b): Conv1d(20, 20, kernel_size=(4,), stride=(1,))
(gap1): AvgPool1d(kernel_size=(192,), stride=(192,), padding=(0,))
(do1): Dropout(p=0.2, inplace=False)
(fc0): Linear(in_features=20, out_features=32, bias=True)
(do2): Dropout(p=0.3, inplace=False)
(fc1): Linear(in_features=32, out_features=8, bias=True)
(do3): Dropout(p=0.3, inplace=False)
(fc2): Linear(in_features=8, out_features=1, bias=True)
)

## Slide 22: Evaluate Network Performance with MCC
Network performance is evaluated using Matthews Correlation Coefficient (MCC) between the predicted and observed response. The MCC is given by: where TP is the number of true positives, TN the number of true negatives, FP the number of false positives, and FN the number of false negatives.
Matthews Correlation Coefficient is an apt metric to assess a binary classification network, especially one with a highly unbalanced class where metrics like accuracy, precision, and recall don’t adequately capture the effectiveness of a network.

## Slide 23: Use k-Fold CV to Ensure Model Robustness to Test/Train Splits
Use Ensemble k-Fold Cross-Validation to Validate Model Robustness to Test-Train Splits
  Splits the data into k parts, Take k-1 parts as training data and 1 part for validation
  Train and predict with the model k times over, holding out a different part each time.
  Ensemble output produces probability of sample belonging to a class, not assignment
  Average and use the prediction probabilities from the k scores to assign a class
Train
Train
Train
Train
Test
Train
Train
Train
Train
Test
Train
Train
Train
Train
Test
Train
Train
Train
Train
Test
Train
Train
Train
Test
Train
k=1
k=2
k=3
k=4
k=5
An example of 5-fold Cross Validation.
For each iteration, fit the model on the training folds and evaluate it using the test fold.
Retain the evaluation scores and probabilities between iterations but discard the trained model.

## Slide 24
Results – Distribution of Public Leaderboard Scores
Top Scores
0.800
0.788
0.786
Machine Learning
MCC = 0.517 local test set
MCC = 0.453 on withheld set
Deep Learning
MCC = 0.705 local test set
Users replicating a successful approach
1083 Total Teams
Notes: 1083 teams
c_train = confusion(y_pred_train > 0, data.y_train)
true_positives, false_positives, true_negatives, false_negatives
print(c_train) # (212, 118, 7658, 287)
print(mcc(*c_train)) # 0.49838358624446083
c_val = confusion(y_pred_val > 0, data.y_val)
true_positives, false_positives, true_negatives, false_negatives
print(c_val) # (16, 3, 407, 10)
print(mcc(*c_val)) # 0.7053190215817398

## Slide 25: Interesting Observations and Lessons
Use the right performance metric
  Traditional metrics like accuracy, precision, recall, and F1 scores can be misleading
  Matthews Correlation Coefficient – an effective binary classification performance measure - even for classes of very different sizes.
  Pearson’s Chi-Squared Test - a similar metric for higher order classification problems
Account for the influence of test-train splits
  With so few samples belonging to one of the classes, results can vary wildly
  Rerun analyses while varying splits and random states to find robust performance predictions.
  StratifiedShuffleSplit helps here, returning stratified randomized folds that preserve the percentage of records for each class.
Use a model or framework built for the task, and tune it properly
  Some models are more adept at handling unbalanced classes than others
  Modify and iterate on the impact of class weights, don’t rely on defaults
  Ensemble Cross-Validation – robust test-train splits, produces probabilities not classes
  Use Probabilities of Class Assignment to Under or Over Predict a Class

## Slide 26: Possible Paths to Improve this Project
Move from Detection in Single Cycles to an Accumulator or N-Cycle Detection
  Detect persistent faults while mitigating sporadic effects like corona
  Data should already exist: signal data is device or location tagged
Perform Classification at the Measurement level instead of Signal Level
  While not globally true, when a fault is present in one phase, the likelihood of fault present in one or both or the other phases is high – 90.3%.
  Potentially trades a significant reduction in available training data points for improved classification
Data augmentation
  Using discarded sections as additional null target data – further imbalances class distribution
  A second pass with different slicing and windowing
  Take signals with known faults, use them to synthesize new signals
Revisit Recurrent Neural Networks – LSTM
  Take pre-processed signal, and window around the region dense with peaks to further trim signal length
  Investigate the use of a compressive sampler to further reduce the time series if needed
Notes:   Measurements with no faults present: 2710 (93.3% of measurements exhibit no fault)
  Measurements with fault present in only 1 phase: 19 (9.7% of cases where faults present)
  Measurements with faults present in 2 of 3 phases: 19 (9.7% of cases where faults present)
  Measurements with faults present in all 3 phases: 156 (80.4% of cases where faults present)
True positives for PD … 8187 Signals without Fault, 213 true positives

## Slide 27: References
Misak, S., et al. “A Complex Classification Approach of Partial Discharges from Covered Conductors in Real Environment.” IEEE Transactions on Dielectrics and Electrical Insulation, vol. 24, no. 2, 2017, pp. 1097–1104., doi:10.1109/tdei.2017.006135.
Vantuch, Tomas. Analysis of Time Series Data, 2018, dspace.vsb.cz/bitstream/handle/10084/133114/VAN431_FEI_P1807_1801V001_2018.pdf.
My Kaggle kernel and GitHub repos have been set public:
  Kaggle Kernel: https://www.kaggle.com/jeffreyegan/vsb-power-line-fault-detection-approach
  GitHub: https://github.com/jeffreyegan/VSB_Power_Line_Fault_Detection

## Slide 28: Thank you!

## Slide 29: Modify Class Weights used in Model Training to Remove Bias
Set and Tune Class Weights
  Enables cost-sensitive learning to remove a bias favoring the dominant class
  Impose a costly penalty on minority class misclassification
  Initially set weights based on ratios of data points in each class
  Iterations on tailoring the weights can improve model performance
Example from this Project
  Default Weights are Uniform:
  class_weight = dict({0:1.0, 1:1.0}) # default weights
  Initial set the weights based on ratio of samples in training data.
  Recall 213 / 8712 signals have faults present thus set fault weight 8499/2134 = 39.90
  class_weight = dict({0:1.0, 1:39.9}) # initial, adjusted weights
  Iterate and optimize weights through Monte Carlo analysis
  class_weight = dict({0:0.5, 1:2.0}) # optimized, adjusted weights

## Slide 30: Adjust Thresholds Used for Class Prediction
Adjust Thresholds on Classification Probabilities to Over/Under Predict a Class
  Another method to improve minority class performance
  Default threshold is 0.5 for binary classification,
  Use sklearn.metrics.roc_curve to find and set more appropriate thresholds
    fpr, tpr, thresholds = metrics.roc_curve(y, y_prob, pos_label=1)
  In the final Partial Discharge detection model, the threshold is set to 0.85
Example ROC & Threshold with Balanced Classes
Setting Threshold for Imbalanced Class
Threshold = 0.85
Notes: Still Exaggerated but Curves More Representative of PD Data

## Slide 31: Concerns with Training/Test Splits on Unbalanced Data
Perform Monte Carlo trials that vary the random_state and test_size parameters in sklearn’s train_test_split function and assess the impact of different thresholds on performance.
The goal is to find and set thresholds for Peak Detection and Fault Classification that routinely yield higher Matthews Correlation Coefficient scores and are robust to varied divisions of the training data.
Notes: Initial submissions proved less than spectacular, my localized training used a fixed random_state (my usual preference for repeatability) that happened to put me at the high end of these types of plots.
I has also used a standard 80-20 split, …
Goal here was to find some thresholds (both for peak detection and fault classification) that routinely yielded greater MCC scores and that was robust to varied splitting of the training data.

## Slide 32: Revisiting Random Forest – Tuning for Unbalanced Classes
Use Ensemble k-Fold Cross-Validation
  Splits the data into k parts, Take k-1 parts as training data and 1 part for validation
  Train and predict with the model k times over, holding out a different part each time.
  Ensemble output produces probability of sample belonging to a class, not assignment
  Average and use the prediction probabilities from the k scores to assign a class
Set and Tune Class Weights
  Enables cost-sensitive learning to remove a bias favoring the dominant class
  Impose a costly penalty on minority class misclassification
  Initially set weights based on ratios of data points in each class
  Iterations on tailoring the weights can improve model performance
Adjust Thresholds on Classification Probabilities to Over/Under Predict a Class
  Another method to improve minority class performance
  Adjust probability thresholds for making a classification